PERIODIC INSPECTION OF PORTABLE ELEC EQPT

INSPECTION DATE:

FORM NO.

| TYPE OF EQPT | PORTABLE GENERATOR SET |
| --- | --- |
| TAG NO. |  |  |  |
| MAKE |  | SL.NO. |  |
| MODEL NO. |  |  |  |
| LOCATION OF THE MC AT THE TIME OF INSPN |  |  |
| NAME OF THE CONTRACTOR |  |  |
| CONTRACT SUPERVISOR NAME |  |  |
| CONTACT NO. |  |  |

Please fill in the below check list and mention clearly the non-compliance if any in the remarks column.

| S.No. | Checking parameter | OK | NOT OK | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Battery condition |  |  |  |
| 2 | Battery terminal connection |  |  |  |
| 3 | Securing of battery |  |  |  |
| 4 | Battery dynamo condition and wiring tightness. |  |  |  |
| 5 | Negative grounding of battery |  |  |  |
| 6 | All individual cell caps are intact |  |  |  |
| 7 | Starter motor condition |  |  |  |
| 8 | Starter motor terminal connection |  |  |  |
| 9 | Starter motor solenoid condition |  |  |  |
| 10 | Alternator enclosure |  |  |  |
| 11 | Pilot exciter enclosure |  |  |  |
| 12 | Coupling guard is available? |  |  |  |
| 13 | Carbon brush condition ( Insist to run the machine and check for sparking within limits. If heavy sparking is observed the machine should not be allowed to run) |  |  |  |
| 14 | Carbon brush holder and spring tension |  |  |  |
| 15 | Main frame grounding |  |  |  |
| 16 | Neutral grounding. Mention how the neutral is grounded in the remarks column. |  |  |  |
| 17 | Grounding of associated panel |  |  |  |
| Mechanical parameters |  |  |  |
| 18 | Main base frame condition and fixing bolts |  |  |  |
| 19 | Condition of acoustic enclosure |  |  |  |
| 20 | Overall engine condition |  |  |  |
| 21 | Spark arrestor in the exhaust |  |  |  |
| 22 | Spark arrestor validity. Note: The spark arrestors should be inspected and validated by cairn HSE periodically. |  |  |  |
| 23 | Diesel tank. Check for leak and cap. |  |  |  |
| 24 | Radiator overall condition. |  |  |  |
| 25 | Check for radiator water leak |  |  |  |
| 26 | Radiator water level |  |  |  |
| 27 | Run the engine and check for vibration |  |  |  |
| 28 | Metering panel condition and reading. The fuel, lube oil pressure, lube oil temperature and water temperature meters should be functional and abnormal values should trip the engine. Check for the tripping function |  |  |  |
| 29 | Emergency Stop available |  |  |  |
| Distribution Panel |  |  |  |
| 30 | Distribution panel condition. Ensure securing of panel cover / enclosure with all bolts without any gap. |  |  |  |
| 31 | The cable termination at alternator and distribution panel end with proper glands and lugs |  |  |  |
| 32 | Spare entry holes of distribution panel covered |  |  |  |
| 33 | The Main SFU / MCCB / ELMCB is of proper rating. Note if mains have ELCB as control unit an additional MCB is to be in place for short ckt protection. |  |  |  |
| 34 | For generator rating above 10KVA, the cable from generator to distribution panel shall be armoured cable |  |  |  |
| 35 | The outgoing feeders from the distribution panels are provided with ELCBs / ELMCBs of 30mA rating |  |  |  |
| 36 | If the individual outgoing is not provided with ELCBs, then main I/C shall have earth leakage protection of 100mA rating. |  |  |  |
| 37 | ELCB test trip OK / Not OK? |  |  |  |
| Measuring Parameters |  |  |  |
| 38 | IR value of the alternator main winding |  |  | The minimum acceptable value is 5 Meg ohms |
| 39 | IR value of the alternator field winding for gensets 250KVA and above |  |  | To be measured with 100V megger. |
| 40 | Winding resistance of alternator main winding |  |  |  |
| 41 | Neutral to body earth continuity and resistance |  |  |  |
| 42 | Neutral to earth pit earth continuity and resistance |  |  |  |
| 43 | With the engine running measure the phase to phase and phase to neutral voltage values and record the values |  |  |  |
| 44 | Battery voltage when idle |  |  |  |
| 45 | Battery voltage when engine running |  |  |  |
| 46 | Lube oil pressure |  |  |  |
| 47 | Water temperature |  |  |  |

The above points shall be checked thoroughly and in case of any critical non – compliance the machine should not be allowed to operate until the points are complied with.

| Overall condition | OK | NOT OK |
| --- | --- | --- |
| Give brief reasons for Not OK: |
| In case of Not OK, ensure the machine is moved away from the process area and the corrective action is being taken. Inform the respective contractor and CEIL department superintendents |

Next Due date for inspection:

Suggested corrective actions:

Inspected by

| Inspected by | Name | Signature |
| --- | --- | --- |
| Elec Engineer |  |  |
| Mech Engineer |  |  |
| HSE Engineer |  |  |
| Contract representative |  |  |